## Slide 1: Lecture 2 of 4 (24:1)
Physics 524 Survey of Instrumentation & Laboratory Techniques:
Unit 5: Cooling & Thermal management

## Slide 2: 5.3 Phase Change Cooling (here seawater)
Solid fresh water melts, cooling sea water (water with around 35 kg/tonne of salt)
(Picture credit: TheRiderPost.com:
https://www.theriderpost.com/lifestyle/environnement/iceberg-titanic-sechoue-cote-canada/ )

## Slide 3: 5.3 Phase Change Cooling
We saw in the examples of some of the heat exchangers that a
phase change can occur in one of the fluids.
Changing the phase of a fluid requires the right combination of
temperature & pressure, and requires a lot of energy transfer
to achieve.
Indeed: phase change is a very good way to achieve cooling
with a much smaller flow of coolant than in a monophase system.
We will now go on to explore the energy uptake capabilities
of phase change cooling.

## Slide 4: Attention: ye approach Isenthalp

## Slide 5: 5.3 Phase Change Cooling (2)
A kitchen crisis…
Materials can contain a huge amount of energy, and we are not talking about E = mc2 (we wont).
Your kitchen kettle holds 1 litre of water and has a power rating of 2000 Watts.
(You can ignore the loss of heat through the kettle wall to the kitchen for now).
You fill it and turn it on noticing that the kitchen temperature is 20 ˚C.
In just under 3 minutes on the kitchen clock (167 seconds later) the water is boiling and bubbling nicely: 1 kg of water has been raised 80 ˚C for a total delivered electrical energy of 334.7 kilojoules
(It already sounds like a lot: did you need all this energy just to boil water for one cup of mint tea?).
The bell rings: somebody’s at the front door and you forget to switch off the kettle, which doesn’t have an automatic cut out at 100 ˚C. Some time later you smell a nasty smell coming from the kitchen, which is full of steam. The kettle is empty and finally its thermal interlock trips. You look at the kitchen clock and see that almost 19 more minutes have passed!
Q: How much extra energy was wasted boiling that water into steam at 100 ˚C while you were outside?
A: around 2.25 Mega Joules*! (or about 0.1% of the output of a typical 2GW electrical power station for 1 second). This is around eight times more than you used to raise the liter of water to its boiling temperature for that cup of tea.
*The amount is calculated from the 2250 kJ.kg-1 latent heat (or “enthalpy”) of evaporation, of water
at atmospheric pressure (1 bar) where the evaporation temperature is 100 ˚C.

## Slide 6: 5.3 Phase Change Cooling (3)
So what is enthalpy: - in thermodynamic terms?
Well, the key here is in the “dynamics” of the word “thermodynamics”.
Thermodynamics is the study of changes in key parameters of material systems:
pressure, temperature and energy being carried, in response to perturbations applied to
the system caused by the delivery of external heat energy, the extraction of energy from
the system and by the application of mechanical work to the system, or indeed making
the system perform mechanical work.
Enthalpy (H) is usually expressed in terms of the internal energy (E) of a system and its
temperature T, volume V, and pressure P. for example:
H = E + P.V
The internal energy of a system is hard to measure directly. The energy carrying capability
of fluids depends on factors including their chemical composition. Surprisingly, water
(mol. wt. 18) has a much higher heat capacity (4181 J.kg-1.K-1 @25˚C ) than cooling fluids
with higher molecular weights. Its enthalpy of evaporation is also much higher.
The absolute enthalpy, H, of a system can perhaps be thought of as containing a baseline
energy on top of which energetic changes (thermodynamic changes) of interest occur.
In terms of a particular material it can be expressed in kJ.kg-1.

## Slide 7: 5.3 Phase Change Cooling (4)
Pressure-enthalpy diagram: example: for a domestic refrigerator closed-loop cycle (R404A):
(DA): heat extraction (enthalpy increase) - evaporation at -20 ˚C;
(A1B) vapour compression (temperature & pressure increase through mechanical work)),
(BC) condensation (enthalpy decrease) at 43 ˚C (hot condenser radiator of refrigerator);
(C1D) liquid “detent” (Joule-Thompson cooling through forced pressure drop at constant
enthalpy) through a throttling element like an orifice, valve or thin tube (capillary).
P-h diagram calculated with REFPROP Standard reference database 23, version 9.0 (2010):
E. Lemmon, M. Huber, & M. McLinden U.S. National Institute of Standards & Technology
R404A
Isenthalp

## Slide 8: 5.3 Phase Change Cooling (5)
Path (DA): shows the that difference in enthalpy necessary to evaporate 1 kg of R404A
between points D (360 kJ.kg-1) & A (245 kJ.kg-1) is 115 kJ.kg-1 on the enthalpy axis.
This enthalpy difference of tells us the refrigerative (here evaporative) power ERPP,T (W)
that a mass flow of 1 kg.s-1 of this fluid can remove at these conditions of
(constant) temperature and pressure, as follows:
ERP = dHP,T * ṁ
where ṁ is the mass flow in kg.s-1
.The mass flow ṁ of refrigerant necessary for required refrigerative power ERP is thus:
ṁ = ERP/dHP,T
For example, a domestic refrigerator must evaporate 2.6 grams per second of R404A
for a refrigerative power of 300 Watts in the conditions of transition DA above.
R404A

## Slide 9: 5.3 Phase Change Cooling (6): LHC ATLAS detector with C3F8 coolant
Compression
Another way of looking at energy exchange: Digger = fluid; heat in vapour form = sand...
On-detector
evaporation
Condensation at 17 bar
Vapour compression
Liquid supply & detent
C3F8

## Slide 10: Let’s digress! Here is ATLAS at LHC

## Slide 11: Unpeeling the ATLAS Onion

## Slide 12: Unpeeling the ATLAS Onion: the evaporators ‘Semi-Conductor Tracker’ (SCT) silicon microstrip tracker surrounding pixel detector
SCT + pixels: 204 C3F8 evaporative cooling circuits
60kW total power to evacuate (1.2 kgs-1 C3F8)

## Slide 13: Unpeeling the ATLAS Onion: the evaporators ATLAS – Silicon Pixel Detector Structure
~50 Horizontal stave cooling channels (l ~ 1,60m)
18 “radial” channels: disk sectors

## Slide 14
5.3 Phase Change Cooling (7): LHC ATLAS Pixel & SCT detector cooling
with evaporating C3F8 : you’ve just seen the evaporators;
now the other parts of the system (including the problematic compressors)
Compression

## Slide 15
Condensation @-60ºC
On –detector Evaporation @-25ºC
Animation: Digger = fluid; heat in vapour form = sand...
5.3 Phase Change Cooling (8):
Let’s get rid of the compresssors and do it in reverse with no moving parts!

## Slide 16: 5.3 Phase Change Cooling (9): The ATLAS Si tracker C3F8 92 m (300’) thermosiphon cooling system: no moving parts (except valves) in C3F8 circuit.

## Slide 17
Compressors kept as backup solution
EXTERNAL PART
INTERNAL PART
Gravity-driven thermosiphon evaporative cooling system
92m pit depth at ATLAS  > 13 bar (rgh) hydrostatic pressure liquid C3F8 or C3F8/C2F6
rgh from 92m of C3F8 vapour is only ~70mbar …
not difficult to return vapour to a cold condenser on the surface, but condenser must be highest geographic - but lowest temperature & pressure - component

## Slide 18: Thermosiphon: Reversal on Pressure-Enthaply Diagram
Gravity thermosiphon driven
Compressor driven

## Slide 19: 5.3 Phase Change Cooling (10):

## Slide 20: 5.3 Phase Change Cooling (11):
* Liquid C6F14 is used to condense C3F8 vapor at around -60 °C

## Slide 21: 5.3 Phase Change Cooling:
Problem (3) on the ATLAS thermosiphon see also separate sheet:
From the previous slide it is clear that a large number of tubes are needed to condense
Approximately 1.2 kgs-1 of C3F8 to cool the ATLAS silicon tracker. This implies that a
high mass flow of C6F14 liquid is needed, but what this mass flow (kg.s-1)?
Hints to solve this problem:
Looking at the thermosiphon cycle diagram superimposed on the C3F8 p-H diagram, and
particularly at path CD we see that considerable thermal energy has to be extracted from
the C3F8 vapor (in the condenser) to reduce its temperature from around 20 ˚C
(the temperature acquired in ascending through more than 92 meters of pipe to the condenser)
to -60 ˚C, where phase change can occur under the “dome”.
Moving left from the saturated vapour boundary of the dome all energy goes into
condensing the C3F8.
You should therefore use the entire CD enthalpy difference in your calculation;
The specific heat capacity of C6F14 in the range -60  -65 ˚C is around 925 J.kg-1.
C6F14 remains a liquid and does not change phase during this process, but heats up by 5 ˚C.

## Slide 22
Condensation @-60ºC
On –detector Evaporation @-25ºC
5.3 Phase Change Cooling (12.2):
Problem on the ATLAS thermosiphon see also separate sheet
(Diggers removed to make the cycle on the C3F8 ph diagram easier to read)
C3F8

## Slide 23
Credit: reliance home comfort Inc.
https://reliancehomecomfort.com/learning-centre/cool-science-behind-heat-pumps/

## Slide 24
The special component: a (usually
electric – driven) fluid “4-way switch”
D
A
B
C
D
A
B
C
B
A
C
D
B
C
D
A
COMP
COMP
E.D.
E.D.
(Evaporator)
(Evaporator)
(Condenser)
(Condenser)
Electrical analogs