## Slide 1
Sensing Current in Electric Vehicle Supply Equipment
Prof. Olga Mironenko
Department of Electrical and Computer Engineering
Spring 2024
https://transparencyjournal.com/vehicle-grid-v2g-technology-improves-battery-life-evs-study/

## Slide 2
Traditional centralized power system
Distributed power system
DC injection danger for the grid!!
Gertman, Lars, Per Karlsson, and Olof Samuelsson. "On DC Injection to AC Grids from Distributed Generation." LTH/IEA, Lund University, Lund, Sweden, 2005.
“Limitation of DC injection”,
IEEE 1547-2018: Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces
Notes: fix

## Slide 3
Electric Vehicle (EV) as a Distributed Energy Resource or Vehicle-to-Grid (V2G)
Electric Vehicle Supply Equipment (EVSE)
http://www.mdpi.com/1996-1073/10/11/1880/htm
Operator
Operator
EVSEs must verify
the DC injection level
Notes: fix

## Slide 4
DC injection detection
A single device = cost reduction
Today’s Current Sensor capabilities:
(BCT-013-200 Current transformer)
For utility: High accuracy AC current metering
  up to 200A AC
  Accuracy is 0.1%
For grid protection: unable to detect DC current
 | Single-phase EVSE (19.2 kW) | Three-phase EVSE (100 kW)
 | 80 A | 120 A
Voltage | 240V (US), 230V(Europe) | 230V/400V (Europe), 277V/480V (US), 347V/600V (Canada)
AC current metering accuracy class | 0.5, 1.0, 2.0 | 
 | Single-phase EVSE (19.2 kW) | Three-phase EVSE (100 kW)
 | 80 A | 120 A
Voltage | 240V (US), 230V(Europe) | 230V/400V (Europe), 277V/480V (US), 347V/600V (Canada)
AC current metering accuracy class | 0.5, 1.0, 2.0 | 
1
1. The accuracy criteria for revenue metering are described in NIST HB-44, ANSIC12.20 and IEC 62053-11 standards
High accuracy AC current measurements
Notes: fix

## Slide 5
For utility: High accuracy AC current metering
  0.5% or less
  Current rating: ≥ 120A AC
For grid protection: DC detection capability:
  DC injection limit is 0.5% of (400mA or 600 mA)
Mass production of EVSE requires a cost-effective solution
  low cost
Selecting the new current sensor based on following requirements:
The DC injection limit is defined according to “Limitation of DC injection” section of IEEE 1547-2018 standard.
Notes: fix

## Slide 6
Current sensing techniques overview
1. Shunt
Pros | Simplicity  Low cost  AC+DC current  AC ≥ 120A? YES 
Cons | Losses Heat No galvanic isolation
Accuracy | 0.1%, 0.25%, 0.5% 
https://www.allaboutcircuits.com/textbook/direct-current/chpt-8/ammeter-design/
Shunt resistor operating principle.

## Slide 7
2. Rogowski coil.
Pros | Simplicity Flexibility Cost-effectiveness Galvanic isolation Linearity AC ≥ 120A? YES 
Cons | AC current only  Integrator is required at the output
Accuracy | 1% 
https://www.hioki.com/en/products/listUse/?category=17
Rogowski coil operating principle.
Current sensing techniques overview

## Slide 8
3. Current transformer (CT).
 | CT
Pros | - Simplicity Low losses No amplification is required at the output Galvanic isolation AC ≥ 120A? YES 
Cons | - AC current only 
Accuracy | - 0.1% 
CT operating principle.
Current sensing techniques overview
https://en.wikipedia.org/wiki/Current_transformer

## Slide 9
4. Hall-Effect Sensors.
Hall-Effect
Hall-effect current sensor structure
https://sensing.honeywell.com/index.php?ci_id=51431
Current sensing techniques overview
Thin conductive material

## Slide 10
4. Hall-Effect Sensors.
Pros | AC+DC current  Low losses Galvanic isolation AC ≥ 120A? YES 
Cons | High cost  Lack of accuracy at low currents (for sensors with > 100A) 
Accuracy | - 0.05% - 2% 
Pros | AC+DC current  Low losses Galvanic isolation AC ≥ 120A? YES 
Cons | 
Accuracy | - 0.05% - 2% 
Current sensing techniques overview
LEM Hall-Effect sensor LA 150-P, LEM datasheet

## Slide 11
5. Fluxgate Sensors: working principle.
http://www.imperial.ac.uk/space-and-atmospheric-physics/research/areas/space-magnetometer-laboratory/space-instrumentation-research/magnetometers/fluxgate-magnetometers/how-a-fluxgate-works/ ;
Twin - rod fluxgate
(Vacquier fluxgate)
Ring core fluxgate
Current sensing techniques overview
Basic fluxgate sensor

## Slide 12
Pros | AC+DC current  Low losses Galvanic isolation AC ≥ 120A? YES 
Cons | High cost  High complexity 
Accuracy | - up to 0.0002% 
5. Fluxgate Sensors: pros and cons.
Current sensing techniques overview
LEM fluxgate sensor CTSR 0.3-P, LEM datasheet

## Slide 13
6. Magneto Resistance Effect sensors.
Resistance varies as a function of applied magnetic field.
Current sensing techniques overview
Anisotropic Magneto Resistance (AMR) Sensors
F.W. Bell AMR current sensors
Pros | AC+DC current AC ≥ 120A? YES 
Cons | High cost  Mounting 
Accuracy | - 0.8% 
Ferromagnetic strip
Ferromagnetic strip
I
I
No external magnetic field
Applied external magnetic field
Magneto-resistive current sensors for peak currents up to 150a. Tech. Rep.; F.W. Bell

## Slide 14
6. Magneto Resistance Effect sensors.
Current sensing techniques overview
Giant Magneto Resistance (GMR) Sensors
Pros | AC+DC current  Low cost 
Cons | Mounting  Low current applications 
Accuracy | - 2% 
Ferromagnetic
Ferromagnetic
Ferromagnetic
Ferromagnetic
Thin conductor
I
I
No external magnetic field
High resistance
Applied external magnetic field
Low resistance
Acs70331: High sensitivity, 1 MHz, GMR-based current sensor IC in space-saving low resistance QFN and SOIC packages. Tech. Rep.; Allegro microsystems; 2019

## Slide 15
6. Magneto Resistance Effect sensors.
Current sensing techniques overview
Tunneling Magneto Resistance (TMR) Sensors
Pros | AC+DC current  AC ≥ 120A? YES  Low cost 
Cons | Mounting  Complexity 
Accuracy | - 0.5% 
Resistance
External
magnetic field
Free layer
Pinned layer
Insulator
Free layer
Pinned layer
Low current
High current
CotoTechnology, REDROCK 111 TMR magnetic sensor

## Slide 16
Which current sensor is the most suitable for EVSE application?
 | AC+DC | AC ≥ 120A | 0.5% accuracy at | Affordable price | Simplicity and convenient mounting
Shunt |  |  |  |  | 
Rogowski coil | × |  |  |  | 
CT | × |  |  |  | 
Hall-Effect |  |  | × |  | 
Fluxgate |  |  |  | × | 
AMR |  |  | × |  | 
GMR |  | × | × |  | 
TMR |  |  |  |  | ×
 | AC+DC | AC ≥ 120A |  | Affordable price | Simplicity and convenient mounting
Shunt |  |  |  |  | 
Rogowski coil | × |  |  |  | 
CT | × |  |  |  | 
Hall-Effect |  |  | × |  | 
Fluxgate |  |  |  | × | 
AMR |  |  | × |  | 
GMR |  | × | × |  | 
TMR |  |  |  |  | ×