## Slide 1
ECE ILLINOIS
Dr. Karl Reinhard
Power System Dynamic Modeling Notes
1 Feb 2018
Notes: ECE Main Slide

## Slide 2
Details – SynchroPhasors Applied to Synchronous Machines
Synchronous Machine Dynamic Model Simulation
RTDS Simulation with Commercial PMU
Synchronous Machine Dynamics from SynchroPhasor Data ??

## Slide 3
Dynamic Phenomena Time Scales

## Slide 4
Synchronous Machine
Stator
Rotor

## Slide 5
Synchronous Machine
Stator
Rotor

## Slide 6: Power Engineering: Load “sign” Convention (aka “Passive sign convention”)
LOAD SIGN CONVENTION
i (t) into load is ‘+’
p (t) into is ‘+’
v (t) is ‘+’ across load (from entry to exit terminals)
 Load is absorbing Power (i.e. resistor radiating heat)
Detailed sign convention discussion:
https://en.wikipedia.org/wiki/Passive_sign_convention
The Load Sign Convention and Kirchoff’s Laws must
be applied with signs consist with & satisfying:

## Slide 7: THE ROTATING MAGNETIC FIELD… ENABLING ROTATING MACHINES
The rotating magnetic field is created by applying
3 sinusoidal voltages time-shifted by 1/3 of a cycle (120o) to
3 coils positioned 120o apart about the machine axis
THREE 120o SPACE-SHIFTED
COILS
THREE 1/3 CYCLE TIME-SHIFTED
VOLTAGES
Superimposing three time-varying magnetic fields results in a single magnetic field that rotates with time.

## Slide 8
% Full Model
options = odeset('Mass‘,Mass_Matrix,
MaxOrder',5,'MaxStep',.002);
[Full_Mdl_Soln] = ode15s(@Full_Model,
tspan,Init_Cond,options);
MATLAB Application
Solver ODE solver – ode15s
  Stiff Differential-Algebraic Equations; variable time-step
  variable order method
Mass_Vector = [ T_s; %( 9)2*H/(2*pi*60)
T_qoprime; %( 6)T_qoprime
T_qo2prime; %( 7)T_qo2prime
T_A; %(12)T_A
0.0; %(18)Algebraic Eqn (V_t)
0.0; %(19)Algebraic Eqn (V_d)
0.0 %(20)Algebraic Eqn (V_q)
T_doprime; %( 4)T_doprime
T_do2prime; %( 5)T_do2prime
0.0; %( 2)Reduced Sys Alg Eqn
0.0; %( 1)Reduced Sys Alg Eqn
0.0; %(15)Algebraic Eqn (I_d)
0.0; %(16)Algebraic Eqn (I_q)…

## Slide 9
MATLAB’s DAE Structural Analysis Tool
MATLAB’s DAESA Tool
  Differential-Algebraic Equations Structural Analyzer,
  Determines structural index, number of degrees of freedom, constraints, variables to be initialized, and suggests a solution scheme.
MATLAB’s DAESA Tool
  Structural index
  # degrees of freedom
  Constraints
  Variables to be initialized,
  Suggests solution scheme.

## Slide 10
3 Fast Dynamic States

## Slide 11
Machine Flux Linkage Dynamic Response

## Slide 12
11 not so fast Dynamic States (1/2)
Synchronous Generator

## Slide 13
11 not so fast Dynamic States (2/2)
Main Exciter
Stabilizing Transformer
Pilot Exciter
Excitation System
Mechanical Power System
Single Stage Turbine Model
Governor Model
PSV = Steam Valve Psn ( Pressure)
PC = Power change setting
PC = 0 when Open Ckt
RD = Speed Droop Regulation Qty
(Terminal Voltage Control)
(Shaft Speed Control)

## Slide 14
Excitation System Dynamic Response

## Slide 15
Mechanical Dynamic Response

## Slide 16
Algebraic Equations (2/2)
6 Algebraic States
(16)
(17)
(18)
(19)
(20)
(15)
3/13/2018

## Slide 17
Algebraic Equations (2/2)
(19)
(20)
e
Many places on DAE Sys RHS – How to Address in Reduction to 2-Axis Model ??

## Slide 18
Terminal Current Dynamic Response

## Slide 19
Terminal Voltage Dynamic Response – dqo

## Slide 20
Solution Check –

## Slide 21
RTDS Model Development Interface

## Slide 22
RTDS Synchronous Generator

## Slide 23
RTDS Transmission Line Model
(Kundur Table 6.1, 10km)
Surge Impedance Load – 140 MW
Zc = 380 W
Z @ 10 km | [pu] | Z_base =
 |  | 9.531E+01
R: |  | 
1.154E-02 | 6.077E-03 | 6.088E-03
6.075E-03 | 1.152E-02 | 6.077E-03
6.088E-03 | 6.077E-03 | 1.154E-02
X: |  | 
9.880E-02 | 4.775E-02 | 4.774E-02
4.775E-02 | 9.883E-02 | 4.775E-02
4.775E-02 | 4.775E-02 | 9.880E-02
L: |  | 
2.50E-02 | 1.21E-02 | 1.21E-02
1.21E-02 | 2.50E-02 | 1.21E-02
1.21E-02 | 1.21E-02 | 2.50E-02

## Slide 25
RTDS Control and Simulation Interface

## Slide 26
RTDS Exciter System
Main Exciter
Pilot Exciter
Excitation System
(Terminal Voltage Control)
Stabilizing Transformer

## Slide 27
RTDS Excitation System Dynamic Response

## Slide 28
RTDS Governor System
Mechanical Power System
Single Stage Turbine Model
Governor Model
PSV = Steam Valve Psn ( Pressure)
PC = Power change setting
PC = 0 when Open Ckt
RD = Speed Droop Regulation Qty
(Shaft Speed Control)

## Slide 29
RTDS Mechanical Dynamic Response

## Slide 30
Terminal Current Dynamic Response

## Slide 31
Terminal Voltage Dynamic Response – dqo

## Slide 32
Synchrophasor Computation

## Slide 33
Synchrophasors Off Fundamental Frequency
Phadke, Arun G., and John Samuel Thorp. Synchronized phasor measurements and their applications. Springer Science & Business Media, 2008.
Measurement error due to
off-nominal frequency

## Slide 34
Synchrophasor Measurement During a Disturbance
Phadke, Arun G., and John Samuel Thorp. Synchronized phasor measurements and their applications. Springer Science & Business Media, 2008.

## Slide 35
Terminal Voltage Dynamic Response – abc frame

## Slide 36
RTDS Synchrophasor Measurements

## Slide 37
Terminal Voltage Dynamic Response

## Slide 38
Breaker Opening – unbalanced 3 Phase – abc frame

## Slide 39
Breaker Opening – unbalanced 3 Phase – dqo frame

## Slide 40
Conclusions
“How does Synchrophasor data relate to the output of the dynamic model in simulation?”
As expected, Synchrophasor do discard most high frequency data
But dynamic phenomena is retained – in the transient stability region
Reduced order model (2 damper winding) has similar impact on data measurements…. The integral manifold is a filter.

## Slide 41
QUESTIONS?
Karl Reinhard
reinhrd2@illinois.edu
reinhardke@gmail.com

## Slide 42
Synchrophasor Concept