## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 11: Synchronous Machines Models and Exciters

## Slide 2: Announcements
Homework 3 is on the website and is due on Feb 27
Read Chapters 6 and 4
Midterm exam is on March 13 in class
  Closed book, closed notes
  You may bring one 8.5 by 11" note sheet
  Simple calculators allowed

## Slide 3
Full model with stator transients
Sub-transient model
Two-axis model
One-axis model
Classical model (const. E behind
)
Summary of Five Book Models

## Slide 4: Two-Axis vs Flux Decay
For 4 bus system, figure compares gen 4 rotor angle for bus 3 fault, cleared at t=1.1 seconds

## Slide 5: Industrial Models
There are just a handful of synchronous machine models used in North America
  GENSAL
    Salient pole model
  GENROU
    Round rotor model that has X"d = X"q
  GENTPF
    Round or salient pole model that allows X"d <> X"q
  GENTPJ
    Just a slight variation on GENTPF
We'll briefly cover each one

## Slide 6: Subtransient Models
The two-axis model is a transient model
Essentially all commercial studies now use subtransient models
First models considered are GENSAL and GENROU, which require X"d=X"q
This allows the internal, subtransient voltage to be represented as

## Slide 7: Subtransient Models
Usually represented by a Norton Injection with
May also be shown as
In steady-state w = 1.0

## Slide 8: GENSAL
  The GENSAL model has been widely used to model salient pole synchronous generators
  In the 2010 WECC cases about 1/3 of machine models were GENSAL; in 2013 essentially none are, being replaced by GENTPF or GENTPJ
In salient pole models saturation is only assumed to affect the d-axis

## Slide 9: GENSAL Block Diagram (PSLF)
A quadratic saturation function is used. For initialization it only impacts the Efd value

## Slide 10: GENSAL Initialization
To initialize this model
  Use S(1.0) and S(1.2) to solve for the saturation coefficients
  Determine the initial value of d with
  Transform current into dq reference frame, giving id and iq
  Calculate the internal subtransient voltage as
  Convert to dq reference, giving P"d+jP"q=  "d+  "q
  Determine remaining elements from block diagram by recognizing in steady-state input to integrators must be zero

## Slide 11: GENSAL Example
Assume same system as before, but with the generator parameters as H=3.0, D=0, Ra = 0.01, Xd = 1.1, Xq = 0.82, X'd = 0.5, X"d=X"q=0.28, Xl = 0.13, T'do = 8.2, T"do = 0.073, T"qo =0.07, S(1.0) = 0.05, and S(1.2) = 0.2.
Same terminal conditions as before
    Current of 1.0-j0.3286 and generator terminal voltage of 1.072+j0.22 = 1.0946 11.59 
Use same equation to get initial d

## Slide 12: GENSAL Example
Then And

## Slide 13: GENSAL Example
Giving the initial fluxes (with w = 1.0)
To get the remaining variables set the differential equations equal to zero, e.g.,
Solving the d-axis requires solving two linear equations for two unknowns

## Slide 14: GENSAL Example
Once E'q has been determined, the initial field current (and hence field voltage) are easily determined by recognizing in steady-state the derivative of E'q is zero
Saved as case B4_GENSAL
Saturation coefficients were determined from the two initial values

## Slide 15: GENROU
The GENROU model has been widely used to model round rotor machines
Saturation is assumed to occur on both the d-axis and the q-axis, making initialization slightly more difficult

## Slide 16: GENROU Block Diagram (PSLF)
The d-axis is similar to that of the GENSAL; the q-axis is now similar to the d-axis. Note saturation affects both axes

## Slide 17: GENROU Initialization
Because saturation impacts both axes, the simple approach will no longer work
Key insight for determining initial d is that the magnitude of the saturation depends upon the magnitude of ", which is independent of d
Solving for d requires an iterative approach; first get a guess of d using 3.229 from the book

## Slide 18: GENROU Initialization
Then solve five nonlinear equations from five unknowns
  The five unknowns are d, E'q, E'd,  'q, and  'd
Five equations come from the terminal power flow constraints (giving voltage and current) and from the differential equations initially evaluating to zero
  Two differential equations for the q-axis, one for the d-axis (the other equation is used to set the field voltage

## Slide 19: GENROU Initialization
Use dq transform to express terminal current as
Get expressions for  "q and  "d in terms of the initial terminal voltage and d
  Use dq transform to express terminal voltage as
  Then from
Recall Xd"=Xq"=X" and w=1 (in steady-state)
Expressing complex equation as two real equations
These values will change during the iteration as d changes

## Slide 20: GENROU Initialization Example
Extend the two-axis example
  For two-axis assume H = 3.0 per unit-seconds, Rs=0, Xd = 2.1, Xq = 2.0, X'd= 0.3, X'q = 0.5, T'do = 7.0, T'qo = 0.75 per unit using the 100 MVA base.
  For subtransient fields assume X"d=X"q=0.28, Xl = 0.13, T"do = 0.073, T"qo =0.07
  for comparison we'll initially assume no saturation
From two-axis get a guess of d

## Slide 21: GENROU Initialization Example
And the network current and voltage in dq reference
Which gives initial subtransient fluxes (with Rs=0),

## Slide 22: GENROU Initialization Example
Without saturation this is the exact solution
  Initial values are: d = 52.1, E'q=1.1298, E'd=0.533,  'q =0.6645, and  'd=0.9614
Efd=2.9133
Saved as case B4_GENROU_NoSat

## Slide 23: Two-Axis versus GENROU Response
Figure compares rotor angle for bus 3 fault, cleared at t=1.1 seconds

## Slide 24: GENROU with Saturation
Nonlinear approach is needed in common situation in which there is saturation
Assume previous GENROU model with S(1.0) = 0.05, and S(1.2) = 0.2.
  Initial values are: d = 49.2, E'q=1.1591, E'd=0.4646,  'q =0.6146, and  'd=0.9940
Efd=3.2186
Saved as case B4_GENROU_Sat

## Slide 25: Two-Axis versus GENROU Response

## Slide 26: GENTPF and GENTPJ Models
These models were introduced by PSLF in 2009 to provide a better match between simulated and actual system results for salient pole machines
  Desire was to duplicate functionality from old BPA TS code
  Allows for subtransient saliency (X"d <> X"q)
  Can also be used with round rotor, replacing GENSAL and GENROU
Useful reference is available at below link; includes all the equations, and saturation details
http://www.wecc.biz/library/WECC%20Documents/Documents%20for%20Generators/Generator%20Testing%20Program/gentpj-typej-definition.pdf

## Slide 27: GENSAL Results
Image source :https://www.wecc.biz/library/WECC%20Documents/Documents%20for %20Generators/Generator%20Testing%20Program/gentpj%20and%20gensal%20morel.pdf
Chief Joseph
disturbance playback
GENSAL
BLUE = MODEL
RED = ACTUAL

## Slide 28: GENTPJ Results
Chief Joseph
disturbance playback
GENTPJ
BLUE = MODEL
RED = ACTUAL

## Slide 29: GENTPF and GENTPJ Models
GENTPF/J d-axis block diagram
GENTPJ allows saturation function to include a component that depends on the stator current
Se = 1 + fsat( ag + Kis*It)
Most of WECC machine models are now GENTPF or GENTPJ
If nonzero, Kis typically ranges from 0.02 to 0.12

## Slide 30
Voltage and Speed Control

## Slide 31: Exciters, Including AVR
Exciters are used to control the synchronous machine field voltage and current
  Usually modeled with automatic voltage regulator included
A useful reference is IEEE Std 421.5-2005
  Covers the major types of exciters used in transient stability simulations
  Continuation of standard designs started with "Computer Representation of Excitation Systems," IEEE Trans. Power App. and Syst., vol. pas-87, pp. 1460-1464, June 1968
Another reference is P. Kundur, Power System Stability and Control, EPRI, McGraw-Hill, 1994
  Exciters are covered in Chapter 8 as are block diagram basics

## Slide 32: Functional Block Diagram
Image source: Fig 8.1 of Kundur, Power System Stability and Control

## Slide 33: Types of Exciters
None, which would be the case for a permanent magnet generator
  primarily used with wind turbines with ac-dc-ac converters
DC: Utilize a dc generator as the source of the field voltage through slip rings
AC: Use an ac generator on the generator shaft, with output rectified to produce the dc field voltage; brushless with a rotating rectifier system
Static: Exciter is static, with field current supplied through slip rings

## Slide 34: Brief Review of DC Machines
Prior to widespread use of machine drives, dc motors had a important advantage of easy speed control
On the stator a dc machine has either a permanent magnet or a single concentrated winding
Rotor (armature) currents are supplied through brushes and commutator
Equations are
Taken mostly from ECE 330 book, M.A. Pai, Power Circuits and Electromechanics
The f subscript refers to the field, the a to the armature; w is the machine's speed, G is a constant. In a permanent magnet machine the field flux is constant, the field equation goes away, and the field impact is embedded in a equivalent constant to Gif

## Slide 35: Types of DC Machines
If there is a field winding (i.e., not a permanent magnet machine) then the machine can be connected in the following ways
  Separately-excited: Field and armature windings are connected to separate power sources
    For an exciter, control is provided by varying the field current (which is stationary), which changes the armature voltage
  Series-excited: Field and armature windings are in series
  Shunt-excited: Field and armature windings are in parallel

## Slide 36
(to sync
mach)
Separately Excited DC Exciter
s1 is coefficient of dispersion, modeling the flux leakage

## Slide 37: Separately Excited DC Exciter
Relate the input voltage, ein1, to vfd
Assuming a constant speed w1

## Slide 38: Separately Excited DC Exciter
If it was a linear magnetic circuit, then vfd would be proportional to in1; for a real system we need to account for saturation
Without saturation we can write

## Slide 39
Separately Excited DC Exciter
This equation is then scaled based on the synchronous machine base values

## Slide 40
Separately Excited Scaled Values
Thus we have
Vr is the scaled output of the voltage regulator amplifier

## Slide 41: The Self-Excited Exciter
When the exciter is self-excited, the amplifier voltage appears in series with the exciter field
Note the additional Efd term on the end

## Slide 42: Self and Separated Exciter Exciters
The same model can be used for both by just modifying the value of KE