## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 12: Exciters

## Slide 2: Announcements
Homework 3 is due now
Homework 4 is on the website and is due on March 6
Read Chapter 4
Midterm exam is on March 13 in class
  Closed book, closed notes
  You may bring one 8.5 by 11" note sheet
    You do not need to write down block diagrams or the detailed synchronous machine equations; I'll give you what you need here
  Simple calculators allowed

## Slide 3: Wind Cut-outs, 2/17/14
Graph provided by Tracy Rolstad, Avista

## Slide 4: GenRou, GenTPF, GenTPJ
Figure compares gen 4 reactive power output for the 0.1 second fault

## Slide 5
Voltage and Speed Control

## Slide 6: Exciters, Including AVR
Exciters are used to control the synchronous machine field voltage and current
  Usually modeled with automatic voltage regulator included
A useful reference is IEEE Std 421.5-2005
  Covers the major types of exciters used in transient stability simulations
  Continuation of standard designs started with "Computer Representation of Excitation Systems," IEEE Trans. Power App. and Syst., vol. pas-87, pp. 1460-1464, June 1968
Another reference is P. Kundur, Power System Stability and Control, EPRI, McGraw-Hill, 1994
  Exciters are covered in Chapter 8 as are block diagram basics

## Slide 7: Functional Block Diagram
Image source: Fig 8.1 of Kundur, Power System Stability and Control

## Slide 8: Types of Exciters
None, which would be the case for a permanent magnet generator
  primarily used with wind turbines with ac-dc-ac converters
DC: Utilize a dc generator as the source of the field voltage through slip rings
AC: Use an ac generator on the generator shaft, with output rectified to produce the dc field voltage; brushless with a rotating rectifier system
Static: Exciter is static, with field current supplied through slip rings

## Slide 9: Brief Review of DC Machines
Prior to widespread use of machine drives, dc motors had a important advantage of easy speed control
On the stator a dc machine has either a permanent magnet or a single concentrated winding
Rotor (armature) currents are supplied through brushes and commutator
Equations are
Taken mostly from ECE 330 book, M.A. Pai, Power Circuits and Electromechanics
The f subscript refers to the field, the a to the armature; w is the machine's speed, G is a constant. In a permanent magnet machine the field flux is constant, the field equation goes away, and the field impact is embedded in a equivalent constant to Gif

## Slide 10: Types of DC Machines
If there is a field winding (i.e., not a permanent magnet machine) then the machine can be connected in the following ways
  Separately-excited: Field and armature windings are connected to separate power sources
    For an exciter, control is provided by varying the field current (which is stationary), which changes the armature voltage
  Series-excited: Field and armature windings are in series
  Shunt-excited: Field and armature windings are in parallel

## Slide 11
(to sync
mach)
Separately Excited DC Exciter
s1 is coefficient of dispersion, modeling the flux leakage

## Slide 12: Separately Excited DC Exciter
Relate the input voltage, ein1, to vfd
Assuming a constant speed w1

## Slide 13: Separately Excited DC Exciter
If it was a linear magnetic circuit, then vfd would be proportional to in1; for a real system we need to account for saturation
Without saturation we can write

## Slide 14
Separately Excited DC Exciter
This equation is then scaled based on the synchronous machine base values

## Slide 15
Separately Excited Scaled Values
Thus we have
Vr is the scaled output of the voltage regulator amplifier

## Slide 16: The Self-Excited Exciter
When the exciter is self-excited, the amplifier voltage appears in series with the exciter field
Note the additional Efd term on the end

## Slide 17: Self and Separated Excited Exciters
The same model can be used for both by just modifying the value of KE

## Slide 18: Saturation
A number of different functions can be used to represent the saturation
The quadratic approach is now quite common
Exponential function could also be used

## Slide 19
Steady state
Exponential Saturation

## Slide 20
Given:
Find:
Exponential Saturation Example

## Slide 21
Amplifier
In steady state
Big
There is often a droop in regulation
Voltage Regulator Model
Modeled as a first order differential equation

## Slide 22: Feedback
This control system can often exhibit instabilities, so some type of feedback is used
One approach is a stabilizing transformer
Large Lt2 so It2  0

## Slide 23
Feedback

## Slide 24: IEEE T1 Exciter
This model was standardized in the 1968 IEEE Committee Paper with Fig 1 shown below

## Slide 25: IEEE T1 Evolution
This model has been subsequently modified over the years, called the DC1 in a 1981 IEEE paper (modeled as the EXDC1 in stability packages)
Image Source: Fig 3 of "Excitation System Models for Power Stability Studies," IEEE Trans. Power App. and Syst., vol. PAS-100, pp. 494-509, February 1981
Note, KE in the feedback is the same as the 1968
approach

## Slide 26: IEEE T1 Evolution
In 1992 IEEE Std 421.5-1992 slightly modified it, calling it the DC1A (modeled as ESDC1A)
Image Source: Fig 3 of IEEE Std 421.5-1992
VUEL is a signal from an under- excitation limiter, which we'll cover later
Same model is in 421.5-2005