## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 15: Governors

## Slide 2: Announcements
Midterm exam is on March 13 in class
  Closed book, closed notes
  You may bring one 8.5 by 11" note sheet
    You do not have to write down model block diagram or the synchronous machine differential equations – I'll supply those if needed
  Simple calculators allowed
Covers up to and including exciters, but not governors
After test read Chapter 7

## Slide 3: Best HW4 Result

## Slide 4: Speed and Voltage Control

## Slide 5: Prime Movers and Governors
Synchronous generator is used to convert mechanical energy from a rotating shaft into electrical energy
The "prime mover" is what converts the orginal energy source into the mechanical energy in the rotating shaft
Possible sources: 1) steam (nuclear, coal, combined cycle, solar thermal), 2) gas turbines, 3) water wheel (hydro turbines), 4) diesel/ gasoline, 5) wind (which we'll cover separately)
The governor is used to control the speed
Image source: http://upload.wikimedia.org/wikipedia/commons/ 1/1e/Centrifugal_governor.png

## Slide 6: Prime Movers and Governors
In transient stability collectively the prime mover and the governor are called the "governor"
As has been previously discussed, models need to be appropriate for the application
In transient stability the response of the system for seconds to perhaps minutes is considered
Long-term dynamics, such as those of the boiler and automatic generation control (AG), are usually not considered
These dynamics would need to be considered in longer simulations (e.g. dispatcher training simulator (DTS)

## Slide 7: Power Grid Disturbance Example
Time in Seconds
Figures show the frequency change as a result of the sudden loss of a large amount of generation in the Southern WECC
Frequency Contour
Freq. Hz)

## Slide 8: Frequency Response for Generation Loss
In response to a rapid loss of generation, in the initial seconds the system frequency will decrease as energy stored in the rotating masses is transformed into electric energy
  Solar PV has no inertia, and for most new wind turbines the inertia is not seen by the system
Within seconds governors respond, increasing the power output of controllable generation
  Many conventional units are operated so they only respond to over frequency situations
  Solar PV and wind are usually operated in North America at maximum power so they have no reserves to contribute

## Slide 9: Governor Response: Thermal Versus Hydro
Thermal units respond quickly, hydro ramps slowly (and goes down initially), wind and solar usually do not respond. And many units are set to not respond!
Time in Seconds
Normalized output

## Slide 10: Some Good References
Kundur, Power System Stability and Control, 1994
Wood, Wollenberg and Sheble, Power Generation, Operation and Control (2nd edition, 1996, 3rd in 2013)
IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013
"Dynamic Models for Fossil Fueled Steam Units in Power System Studies," IEEE Trans. Power Syst., May 1991, pp. 753-761
"Hydraulic Turbine and Turbine Control Models for System Dynamic Studies," IEEE Trans. Power Syst., Feb 1992, pp. 167-179

## Slide 11: Control of Generation Overview
Goal is to maintain constant frequency with changing load
If there is just a single generator, such with an emergency generator or isolated system, then an isochronous governor is used
  Integrates frequency error to insure frequency goes back to the desired value
  Cannot be used with interconnected systems because of "hunting"
Image source: Wood/Wollenberg, 2nd edition

## Slide 12: Generator “Hunting”
Control system “hunting” is oscillation around an equilibrium point
Trying to interconnect multiple isochronous generators will cause hunting because the frequency setpoints of the two generators are never exactly equal
  One will be accumulating a frequency error trying to speed up the system, whereas the other will be trying to slow it down
  The generators will NOT share the power load proportionally.

## Slide 13: Isochronous Gen Example
WSCC 9 bus from before, gen 3 dropping (85 MW)
  No infinite bus, gen 1 is modeled with an isochronous generator (new PW v18 ISOGov1 model)
Gen 2 is modeled with no governor, so its mechanical power stays fixed

## Slide 14: Isochronous Gen Example
Graph shows the change in the mechanical output
All the change in MWs due to the loss of gen 3 is being picked up by gen 1

## Slide 15: Droop Control
To allow power sharing between generators the solution is to use what is known as droop control, in which the desired set point frequency is dependent upon the generator’s output
R is known as the regulation constant or droop; a typical value is 4 or 5%.
At 60 Hz and a 5% droop, each 0.1 Hz change would change the output by 0.1/(60*0.05)=
3.33%

## Slide 16: WSCC 9 Bus Droop Example
Assume the previous gen 3 drop contingency (85 MW), and that gens 1 and 2 have ratings of 500 and 250 MVA respectively and governors with a 5% droop. What is the final frequency (assuming no change in load)?

## Slide 17: WSCC 9 Bus Droop Example
The below graphs compare the mechanical power and generator speed; note the steady-state values match the calculated 59.66 Hz value
Case is wscc_9bus_TGOV1

## Slide 18: Quick Interconnect Calculation
When studying a system with many generators, each with the same (or close) droop, then the final frequency deviation is
The online generator summation should only include generators that actually have governors that can respond, and does not take into account generators hitting their limits
The online generators obviously does not include the contingency generator(s)

## Slide 19: Larger System Example
As an example, consider the 37 bus, nine generator example from earlier; assume one generator with 42 MW is opened. The total MVA of the remaining generators is 1132. With R=0.05
Case is Bus37_TGOV1

## Slide 20: Impact of Inertia (H)
Final frequency is determined by the droop of the responding governors
How quickly the frequency drops depends upon the generator inertia values
The least frequency deviation occurs with high inertia and fast governors

## Slide 21: Restoring Frequency to 60 (or 50) Hz
In an interconnected power system the governors to not automatically restore the frequency to 60 Hz
Rather this is done via the ACE (area control area calculation). Previously we defined ACE as the difference between the actual real power exports from an area and the scheduled exports. But it has an additional term ACE = Pactual - Psched – 10b(freqact - freqsched)
b is the balancing authority frequency bias in MW/0.1 Hz with a negative sign. It is about 0.8% of peak load/generation

## Slide 22: 2600 MW Loss Frequency Recovery
Frequency recovers in about ten minutes

## Slide 23
model shaft “squishiness” as a spring
High-pressure turbine shaft dynamics
Turbine Models
Usually shaft dynamics are neglected

## Slide 24
Steam Turbine Models
Boiler supplies a "steam chest" with the steam then entering the turbine through a value
We are assuming d=dHP and w=wHP

## Slide 25
Steam Governor Model

## Slide 26
R = .05 (5% droop)
Steam valve limits
Steam Governor Model

## Slide 27: TGOV1 Model
Standard model that is close to this is TGOV1
Here T1 corresponds to TSV and T3 to TCH
TGOV1 is not commonly used because it is too simple, but it is a good place to start; Dt is used to model turbine damping and is often zero

## Slide 28: IEEEG1
A common stream turbine model, is the IEEEG1, originally introduced in the below 1973 paper
IEEE Committee Report, “Dynamic Models for Steam and Hydro Turbines in Power System Studies,” Transactions in Power Apparatus & Systems, volume 92, No. 6, Nov./Dec. 1973, pp 1904-15
In this model K=1/R
It can be used to represent cross-compound units, with high and low pressure steam
Uo and Uc are rate limits