## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 2: Overview and Electromagnetic Transients

## Slide 2: About Me
Professional
  Received BSEE, MSEE, and Ph.D. all from University of Wisconsin at Madison (83, 88, 91)
  Worked for eight years as engineer for an electric utility (Madison Gas & Electric)
  Have been at UI since 1991, doing teaching and doing research in the area of electric power systems
  Developed commercial power system analysis package, known now as PowerWorld Simulator. This package has been sold to about 600 different corporate entities worldwide
  DOE investigator for 8/14/2003 blackout

## Slide 3: About Prof. Tom Overbye
Nonprofessional
  Married to Jo
  Have three children
    Tim age 19
    Hannah age 16 (almost 17!)
    Amanda age 14
  Live in country by Homer
  We’ve homeschooled our kids all the way through, with Tim now starting his second semester at UIUC in mechanical engineering

## Slide 4: My Kids

## Slide 5
Overview
Electromagnetic transients
Synchronous machine
Excitation and governor modeling
Single machine
Time-scales and reduced-order models
Multi-machine
Transient Stability
Linearization, small signal
Power system stabilizer design
Energy function methods
Course Topics

## Slide 6
Power Systems
Aircraft
Automobiles
Standby power sources
Electric utilities
        Mechanical prime movers
        Electrical generators
        Electrical network
        Electrical loads

## Slide 7: Power System Time Frames
Image source: P.W. Sauer, M.A. Pai, Power System Dynamics and Stability, 1997, Fig 1.2, modified

## Slide 8: Modeling Cautions!
"All models are wrong but some are useful," George Box, Empirical Model-Building and Response Surfaces, (1987, p. 424)
  Models are an approximation to reality, not reality, so they always have some degree of approximation
  Box went on to say that the practical question is how wrong to they have to be to not be useful
A good part of engineering is deciding what is the appropriate level of modeling, and knowing under what conditions the model will fail
Always keep in mind what problem you are trying to solve!

## Slide 9: Transient Stability Example 1
1996: Transient Stability Model Errors Lead to Blackouts

## Slide 10: Transient Stability Example 2
Source: Arizona-Southern California Outages on September 8, 2011 Report, FERC and NERC,April 2012
We’ve come a long ways since 1996 towards improved simulations. Still, a finding from the 2011 Blackout is the simulations didn’t match the actual system response and need to be improved.

## Slide 11: Models and Their Parameters
Models and their parameters are often tightly coupled
  The parameters for a particular model might have been derived from actual results on the object of interest
Changing the model (even correcting an "incorrect" simulation implementation) can result in unexpected results!
Using a more detailed simulation approach without changing the model can also result in incorrect results
  More detailed models are not necessarily more accurate

## Slide 12: Static versus Dynamic Analysis
Statics versus dynamics appears in many fields
An equilibrium point is a point at which the model is not changing
  Real systems are always changing, but over the time period of interest an unchanging system can be a useful approximation
Static analysis looks at how the equilibrium points change to a change in the model
  Power system example is power flow
Dynamic analysis looks at how the system responds over time when it is perturbed away from an equilibrium point
  Power system example is transient stability

## Slide 13: Slow versus Fast Dynamics
Key analysis question in setting up and solving models is to determine the time frame of interest
Values that change slowing (relative to the time frame of interest) can be assumed as constant
  Power flow example is the load real and reactive values are assumed constant (sometimes voltage dependence is included)
Values that change quickly (relative to the time frame of interest) can be assumed to be algebraic
  A generator's terminal voltage in power flow is an algebraic constraint, but not in transient stability
  In power flow and transient stability the network power balance equations are assumed algebraic

## Slide 14: Positive Sequence versus Full Three-Phase
Large-scale electrical systems are almost exclusively three-phase. Common analysis tools such as power flow and transient stability often assume balanced operation
  This allows modeling of just the positive sequence though full three-phase models are sometimes used particularly for distribution systems
  Course assumes knowledge of sequence analysis
Other applications, such as electromagnetic transients (commonly known as electromagnetic transients programs [EMTP]) consider the full three phase models

## Slide 15: Course Coverage
Course is focused on the analysis of the dynamics and stability of high voltage power systems
  Some consideration of general solution methods, some consideration of power system component modeling in different time frames, and some consideration of using tools to solve example larger-scale power system problems
Course seeks to strike a balance between the theoretical and the applied

## Slide 16: PowerWorld Simulator
Class will make extensive use of PowerWorld Simulator. If you do not have a copy of v17, the free 42 bus student version is available for download at
http://www.powerworld.com/gloversarmaoverbye
Start getting familiar with this package, particularly the power flow basics. Transient stability aspects will be covered in class
Free training material is available at
http://www.powerworld.com/training/online-training

## Slide 17: Power Flow Versus Dynamics
The power flow is used to determine a quasi steady-state operating condition for a power system
  Goal is to solve a set of algebraic equations g(x) = 0
  Models employed reflect the steady-state assumption, such as generator PV buses, constant power loads, LTC transformers
Dynamic analysis is used to determine how the system changes with time, usually after some disturbance perturbs it away from a quasi-steady state equilibrium point

## Slide 18: Example: Transient Stability
Transient stability is used to determine whether following a disturbance (contingency) the power system returns to a steady-state operating point
  Goal is to solve a set of differential and algebraic equations, dx/dt = f(x,y), g(x,y) = 0
  Starts in steady-state, and hopefully returns to steady-state.
  Models reflect the transient stability time frame (up to dozens of seconds), with some values assumed to be slow enough to hold constant (LTC tap changing), while others are still fast enough to treat as algebraic (synchronous machine stator dynamics, voltage source converter dynamics).

## Slide 19: Physical Structure Power System Components
P. Sauer and M. Pai, Power System Dynamics and Stability

## Slide 20: Physical Structure Power System Components
Generator
Voltage Control
P, Q
Network
Network control
Loads
Load control
Fuel
Source
Supply control
Furnace and Boiler
Pressure control
Turbine
Speed control
V, I
Torque
Steam
Fuel
Electrical System
Mechanical System
Governor
Machine
Exciter
Load
Char.
Load
Relay
Line
Relay
Stabilizer

## Slide 21
Power Timescales

## Slide 22: Electromagnetic Transients
The modeling of very fast power system dynamics (much less than one cycle) is known as electromagnetics transients program (EMTP) analysis
  Covers issues such as lightning propagation and switching surges
Concept originally developed by Prof. Hermann Dommel for his PhD in the 1960's (now emeritus at Univ. British Columbia)
  After his PhD work Dr. Dommel worked at BPA where he was joined by Scott Meyer in the early 1970's
  Alternative Transients Program (ATP) developed in response to commercialization of the BPA code

## Slide 23: Transmission Line Modeling
In power flow and transient stability transmission lines are modeled using a lumped parameter approach
  Changes in voltages and current in the line are assumed to occur instantaneously
  Transient stability time steps are usually a few ms (1/4 cycle is common, equal to 4.167ms for 60Hz)
In EMTP time-frame this is no longer the case; speed of light is 300,000km/sec or 300km/ms or 300m/ms
  Change in voltage and/or current at one end of a transmission cannot instantaneously affect the other end

## Slide 24
Incremental Transmission Line Modeling
Define the receiving end as bus m (x=0) and the sending end as bus k (x=d)

## Slide 25
Incremental Transmission Line Modeling
We are looking to determine v(x,t) and i(x,t)

## Slide 26
Incremental Transmission Line Modeling
Taking the limit we get
Some authors have a negative sign with these equations; it just depends on the direction of increasing x; note values are function of both x and t

## Slide 27
C' = G' = 0 (neglect shunts)
Special Case 1
This just gives a lumped parameter model, with all electric field effects neglected

## Slide 28
The lossless line (R'=0, G'=0), which gives
This is the wave equation with a general solution of
Special Case 2: Wave Equation
Zc is the characteristic impedance and vp is the velocity of propagation

## Slide 29: Special Case 2: Wave Equation
This can be thought of as two waves, one traveling in the positive x direction with velocity vp, and one in the opposite direction
The values of f1 and f2 depend upon the boundary (terminal) conditions

## Slide 30: Calculating vp
To calculate vp for a line in air we go back to the definition of L' and C' (covered in a course like 476)
With r'=0.78r this is very close to the speed of light

## Slide 31: Important Insight
The amount of time for the wave to go between the terminals is d/vp= t seconds
  To an observer traveling along the line with the wave, x+vpt, will appear constant
What appears at one end of the line impacts the other end t seconds later
Both sides of the bottom equation are constant when x+vpt is
constant

## Slide 32: Determining the Constants
If just the terminal characteristics are desired, then an approach known as Bergeron's method can be used.
Knowing the values at the receiving end m (x=0) we get
This can be used to eliminate f1

## Slide 33: Determining the Constants
Eliminating f1 we get

## Slide 34: Determining the Constants
To solve for f2 we need to look at what is going on at the sending end (i.e., k at which x=d) t = d/vp seconds in the past

## Slide 35: Determining the Constants
Dividing vk by zc, and then adding it with ik gives
Then substituting for f2 in im gives

## Slide 36: Equivalent Circuit Representation
The receiving end can be represented in circuit form as
Notice that the voltage and current at the other end of the line, from t seconds in the past, just look like a current source

## Slide 37: Repeating for the Sending End
The sending end has a similar representation
Both ends of the line are represented by Norton equivalents

## Slide 38: Lumped Parameter Model
In the special case of constant frequency, book shows the derivation of the common lumped parameter model

## Slide 39: Including Line Resistance
An approach for adding line resistance, while keeping the simplicity of the lossless line model, is to just to place ½ of the resistance at each end of the line
  Another, more accurate approach, is to place ¼ at each end, and ½ in the middle
Standalone resistance, such as modeling the resistance of a switch, is just represented as an algebraic equation