## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 26: Modal Analysis, Power System Stabilizers (PSSs)
Special Guest Lecture by TA Soobae Kim

## Slide 2: Announcements
Read Chapters 8 and 9
Homework 8 should be completed before final but need not be turned in
Final is Wednesday May 14 at 7 to 10pm
Key papers for book's approach on stabilizers are
  F.P. DeMello and C. Concordia, "Concepts of Synchronous Machine Stability as Affected by Excitation Control, IEEE Trans. Power Apparatus and Systems, vol. PAS-88, April 1969, pp. 316-329
  W.G. Heffron and R.A. Philips, "Effects of Modern Amplidyne Voltage Regulator in Underexcited Operation of Large Turbine Generators," AIEE, PAS-71, August 1952, pp. 692-697

## Slide 3: Example: Bus 4 with GENROU Model
The eigenvalues can be calculated for any set of generator models
This example replaces the bus 4 generator classical machine with a GENROU model
  There are now six eigenvalues, with the dominate response coming from the electro-mechanical mode with a frequency of 1.83 Hz, and damping of 6.92%

## Slide 4: Example: Bus 4 with GENROU Model and Exciter
Adding an relatively slow EXST1 exciter adds additional states (with KA=200, TA=0.2)
  As the initial reactive power output of the generator is decreased, the system becomes unstable
Case is saved as B4_GENROU_Sat_SMIB

## Slide 5: Example: Bus 4 with GENROU Model and Exciter
With Q4 = 25 Mvar the eigenvalues are
And with Q4=0 Mvar the eigenvalues are

## Slide 6: Example: Bus 4 with GENROU Model and Exciter
Graph shows response following a short fault when Q4 is 0 Mvar
This motivates trying to get additional insight into how to increase system damping, which is the goal of modal analysis

## Slide 7: Modal Analysis - Comments
Modal analysis or analysis of small signal stability through eigenvalue analysis is at the core of SSA software
In Modal Analysis one looks at:
  Eigenvalues
  Eigenvectors (left or right)
  Participation factors
  Mode shape
Power System Stabilizer (PSS) design in a multi-machine context is done using modal analysis method.
Goal is to determine how the various parameters affect the response of the system

## Slide 8: Eigenvalues, Right Eigenvectors
For an n by n matrix A the eigenvalues of A are the roots of the characteristic equation:
Assume l1…ln as distinct (no repeated eigenvalues).
For each eigenvalue li there exists an eigenvector such that:
vi is called a right eigenvector
If li is complex, then vi has complex entries

## Slide 9: Left Eigenvectors
For each eigenvalue li there exists a left eigenvector wi such that:
Equivalently, the left eigenvector is the right eigenvector of AT; that is,

## Slide 10: Eigenvector Properties
The right and left eigenvectors are orthogonal i.e.
We can normalize the eigenvectors so that:

## Slide 11: Eigenvector Example
Right Eigenvectors

## Slide 12: Eigenvector Example
Left eigenvectors
We would like to make
This can be done in many ways.

## Slide 13: Eigenvector Example
It can be verified that WT=V-1 .
The left and right eigenvectors are used in computing the participation factor matrix.

## Slide 14: Modal Matrices
The deviation away from an equilibrium point can be defined as
From this equation it is difficult to determine how parameters in A affect a particular x because of the variable coupling
To decouple the problem first define the matrices of the right and left eigenvectors (the modal matrices)

## Slide 15: Modal Matrices
It follows that
To decouple the variables define z so
Then
Since  is diagonal, the equations are now uncoupled with
So

## Slide 16: Modal Matrices
Thus the response can be written in terms of the individual eigenvalues and right eigenvectors as
Furthermore with
So z(t) can be written as using the left eigenvectors as
Note, we are requiring that
the eigenvalues be distinct!

## Slide 17: Modal Matrices
We can then write the response x(t) in terms of the modes of the system
So Ci represents magnitude of excitation of the ith mode resulting from the initial conditions.

## Slide 18: Numerical example

## Slide 19: Numerical example (contd)

## Slide 20: Numerical example (contd)
Because of the initial condition, the 2nd mode does not get excited

## Slide 21: Mode Shape, Sensitivity and Participation Factors
So we have
x(t) are the original state variables, z(t) are the transformed variables so that each variable is associated with only one mode.
From the first equation the Right Eigenvector gives the “mode shape” i.e. relative activity of state variables when a particular mode is excited.
For example the degree of activity of state variable xk in vi mode is given by the element Vki of the the Right Eigenvector matrix V

## Slide 22: Mode Shape, Sensitivity and Participation Factors
The magnitude of elements of vi give the extent of activities of n state variables in the ith mode and angles of elements (if complex) give phase displacements of the state variables with regard to the mode.
The left eigenvector wi identifies which combination of original state variables display only the ith mode.

## Slide 23: Eigenvalue Parameter Sensitivity
To derive the sensitivity of the eigenvalues to the parameters recall Avi = livi; take the partial derivative with respect to Akj by using the chain rule

## Slide 24: Eigenvalue Parameter Sensitivity
This is simplified by noting that by the definition of wi being a left eigenvector
Therefore
Since all elements of are zero, except the kth row, jth column is 1
Thus

## Slide 25: Sensitivity Example
In the previous example we had
Then the sensitivity of l1 and l2 to changes in A are
For example with

## Slide 26: Participation Factors
The participation factors, Pki, are used to determine how much the kth state variable participates in the ith mode
The sum of the participation factors for any mode or any variable sum to 1
The participation factors are quite useful in relating the eigenvalues to portions of a model
For the previous example P would be

## Slide 27: PowerWorld SMIB Participation Factors
The magnitudes of the participation factors are shown on the PowerWorld SMIB dialog
The below values are shown for the four bus example with Q4 = 0