## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 3: Electromagnetic Transients

## Slide 2: Announcements
Be reading Chapters 1 and 2
Homework 1 is assigned today, due Feb 6; it is on the website
Classic reference paper on EMTP is H.W. Dommel, "Digital Computer Solution of Electromagnetic Transients in Single- and Multiphase Networks," IEEE Trans. Power App. and Syst., vol. PAS-88, pp. 388-399, April 1969

## Slide 3: Numerical Integration with Trapezoidal Method
Numerical integration is often done using the trapezoidal method discussed earlier
  Here we show how it can be applied to inductors and capacitors
For a general function the trapezoidal is
Trapezoidal integration introduces error on the order of Dt3, but it is numerically stable

## Slide 4: Trapezoidal Applied to Inductor with Resistance
For an inductor in series with resistance we have

## Slide 5
Trapezoidal Applied to Inductor with Resistance
This also becomes a Norton equivalent. A similar expression can be developed for capacitors

## Slide 6: RL Example
Assume a series RL circuit with an open switch with R= 200W and L = 0.3H, connected to a voltage source with
Assume the switch is closed at t=0
The exact solution is
R/L=667, so the dc offset decays quickly

## Slide 7
Exact solution:
RL Example Trapezoidal Solution

## Slide 8
t = .0002
i(.0002) = 117.3A
Exact solution
i(.0002) = 117.3A
Solving for i(.0002)
RL Example Trapezoidal Solution

## Slide 9: Full Solution Over Three Cycles

## Slide 10: RL Example with Varying DeltaT

## Slide 11: A Favorite Qual Problem: R=0 Case, with v(t) = Sin(2*pi*60)

## Slide 12: Lumped Capacitance Model
The trapezoidal approach can also be applied to model lumped capacitors
Integrating over a time step gives
Which can be approximated by the trapezoidal as

## Slide 13: Lumped Capacitance Model
Hence we can derive a circuit model similar to what was done for the inductor

## Slide 14
Example 2.1: Line Closing

## Slide 15
Initial conditions: i1 = i2 = v1 = v2 =0
for t < .0001 sec
Example 2.1: Line Closing
Because of finite propagation speed, the receiving end of the line will not respond to energizing the sending end for at least 0.00055 seconds

## Slide 16
Example 2.1: Line Closing

## Slide 17
Need:
Example 2.1: t=0.0001

## Slide 18
Example 2.1: t=0.0001

## Slide 19
Instantaneously
changed from zero
at t = .0001 sec.
Example 2.1: t=0.0001

## Slide 20
Need:
Example 2.1: t=0.0002
Circuit is essentially the same
Wave is traveling down the line

## Slide 21
switch closed
Example 2.1: t=0.0002 to 0.006
With interpolation receiving end will see wave

## Slide 22
Need:
Example 2.1: t=0.0007
(linear interpolation)

## Slide 23
For ti = .0006 (t = .0007 sec) at the sending end
Example 2.1: t=0.0007
This current source will stay zero until we get a response from the receiving end

## Slide 24
Example 2.1: t=0.0007
For ti = .0006 (t = .0007 sec) at the receiving end

## Slide 25: Example 2.1: First Three Cycles
Red is the sending end voltage (in kv), while green is the receiving end voltage. Note the near voltage doubling at the receiving end

## Slide 26: Example 2.1: First Three Cycles
Graph shows the current (in amps) into the RL load over the first three cycles.
To get a ballpark value on the expected current, solve the simple circuit assuming the transmission line is just an inductor

## Slide 27: Three Node, Two Line Example
Graph shows the voltages for 0.02 seconds for the Example 2.1 case extended to connect another 120 mile line to the receiving end with an identical load
Note that there is no longer an initial overshoot for the receiving (green) end since wave continues into the second line

## Slide 28: Example 2.1 with Capacitance
Below graph shows example 2.1 except the RL load is replaced by a 5 mF capacitor (about 100 Mvar)
Graph on left is unrealistic case of resistance in line
Graph on right has R=0.1 W/mile

## Slide 29: EMTP Network Solution
The EMTP network is represented in a manner quite similar to what is done in the dc power flow or the transient stability network power balance equations or geomagnetic disturbance modeling (GMD)
Solving set of dc equations for the nodal voltage vector V with V = G-1I where G is the bus conductance matrix and I is a vector of the Norton current injections

## Slide 30: EMTP Network Solution
Fixed voltage nodes can be handled in a manner analogous to what is done for the slack bus: just change the equation for node i to Vi = Vi,fixed
Because of the time delays associated with the transmission line models G is often quite sparse, and can often be decoupled
Once all the nodal voltages are determined, the internal device currents can be set
  E.g., in example 2.1 one we know v2 we can determine v3

## Slide 31: Three-Phase EMTP
What we just solved was either just for a single phase system, or for a balanced three-phase system
  That is, per phase analysis (positive sequence)
EMTP type studies are often done on either balanced systems operating under unbalanced conditions (i.e., during a fault) or on unbalanced systems operating under unbalanced conditions
  Lightning strike studies
In this introduction to EMTP will just covered the balanced system case (but with unbalanced conditions)
  Solved with symmetrical components

## Slide 32: Modeling Transmission Lines
Undergraduate power classes usually derive a per phase model for a uniformly transposed transmission line

## Slide 33: Modeling Transmission Lines
Resistance is just the W per unit length times the length
Calculate the per phase inductance and capacitance per km of a balanced 3, 60 Hz, line with horizontal phase spacing of 10m using three conductor bundling with a spacing between conductors in the bundle of 0.3m. Assume the line is uniformly transposed and the conductors have a 1.5 cm radius and resistance = 0.06 W/km

## Slide 34: Modeling Transmission Lines
Resistance is 0.06/3=0.02W/km
  Divide by three because three conductors per bundle

## Slide 35: Untransposed Lines with Ground Conductors
To model untransposed lines, perhaps with grounded neutral wires, we use the approach of Carson (from 1926) of modeling the earth return with equivalent conductors located in the ground under the real wires
  Earth return conductors have the same GMR of their above ground conductor (or bundle) and carry the opposite current
Distance between conductors is

## Slide 36: Untransposed Lines with Ground Conductors
The resistance of the equivalent conductors is Rk'=9.86910-7f W/m with f the frequency, which is also added in series to the Rof the actual conductors
Conductors are mutually coupled; we'll be assuming three phase conductors and N grounded neutral wires
Total current in all conductors sums to zero

## Slide 37: Untransposed Lines with Ground Conductors
The relationships between voltages and currents per unit length is
Where the diagonal resistance are the conductor resistance plus Rk' and the off-diagonals are all Rk'
The inductances are with Dkk just the GMR for the conductor (or bundle)
Dkk' is large so Dkm'  Dkk'

## Slide 38: Untransposed Lines with Ground Conductors
This then gives an equation of the form
Which can be reduced to just the phase values
We'll use Zp with symmetrical components