## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 8: Synchronous Machine Modeling

## Slide 2: Announcements
Homework 2 is posted on the web; it is due on Thursday Feb 20
Skim Chapter 4; we'll be returning to this in greater detail later
  Commercial transient stability packages uses a number of different models to represent types of exciters and governors
Read Chapter 5 and Appendix A

## Slide 3: Load Modeling
The load model used in transient stability can have a significant impact on the results
By default PowerWorld uses constant impedance models but makes it very easy to add more complex loads.
The default (global) models are specified on the Options, Power System Model page.
These models are used only when no other models are specified.

## Slide 4: Load Modeling
More detailed models are added by selecting “Stability Case Info” from the ribbon, then Case Information, Load Characteristics Models.
Models can be specified for the entire case (system), or individual areas, zones, owners, buses or loads.
To insert a load model click right click and select insert to display the Load Characteristic Information dialog.
Right click here to get local menu and select insert.

## Slide 5: Dynamic Load Models
Loads can either be static or dynamic, with dynamic models often used to represent induction motors
Some load models include a mixture of different types of loads; one example is the CLOD model represents a mixture of static and dynamic models
Loads models/changed in PowerWorld using the Load Characteristic Information Dialog
Next slide shows voltage results for static versus dynamic load models
Case Name: WSCC_9Bus_Load

## Slide 6: WSCC Case Without/With Complex Load Models
Below graphs compare the voltage response following a fault with a static impedance load (left) and the CLOD model, which includes induction motors (right)

## Slide 7: Under-Voltage Motor Tripping
In the PowerWorld CLOD model, under-voltage motor tripping may be set by the following parameters
  Vi = voltage at which trip will occur (default = 0.75 pu)
  Ti (cycles) = length of time voltage needs to be below Vi before trip will occur (default = 60 cycles, or 1 second)
In this example as you move the clearing time from 0.033 up to 0.040, you will see the motors tripping out on buses 5, 6, and 8 (the load buses) – this is especially visible on the bus voltages plot. These trips allow the clearing time to be a bit longer than would otherwise be the case.
Set Vi = 0 in this model to turn off motor tripping.

## Slide 8: 37 Bus System
Next we consider a slightly larger, 9 generator, 37 bus system. To view this system open case GSO_37Bus. The system one-line is shown below.
To see summary listings of the transient stability models in this case select “Stability Case Info” from the ribbon, and then either “TS Generator Summary” or “TS Case Summary”

## Slide 9: Transient Stability Case and Model Summary Displays
Right click on a line and select “Show Dialog” for more information.

## Slide 10: 37 Bus Case Solution
Graph shows the generator frequency response following the loss of one generator

## Slide 11: Stepping Through a Solution
Simulator provides functionality to make it easy to see what is occurring during a solution. This functionality is accessed on the States/Manual Control Page
Run a Specified Number of Timesteps or Run Until a Specified Time, then Pause.
See detailed results at the Paused Time
Transfer results to Power Flow to view using standard PowerWorld displays and one-lines

## Slide 12: Summary So Far
The model as developed so far has been derived using the following assumptions
  The stator has three coils in a balanced configuration, spaced 120 electrical degrees apart
  Rotor has four coils in a balanced configuration located 90 electrical degrees apart
  Relationship between the flux linkages and currents must reflect a conservative coupling field
  The relationships between the flux linkages and currents must be independent of qshaft when expressed in the dq0 coordinate system

## Slide 13: Two Main Types of Synchronous Machines
Round Rotor
  Air-gap is constant, used with higher speed machines
Salient Rotor (often called Salient Pole)
  Air-gap varies circumferentially
  Used with many pole, slower machines such as hydro
  Narrowest part of gap in the d-axis and the widest along the q-axis

## Slide 14: Assuming a Linear Magnetic Circuit
If the flux linkages are assumed to be a linear function of the currents then we can write
The rotor self- inductance matrix Lrr is independent of qshaft

## Slide 15
L12 = 0
L12 = + maximum
L12 = - maximum
Inductive Dependence on Shaft Angle

## Slide 16: Stator Inductances
The self inductance for each stator winding has a portion that is due to the leakage flux which does not cross the air gap, Lls
The other portion of the self inductance is due to flux crossing the air gap and can be modeled for phase a as
Mutual inductance between the stator windings is modeled as
The offset angle is either 2p/3 or -2p/3

## Slide 17
Conversion to dq0 for Angle Independence

## Slide 18
Conversion to dq0 for Angle Independence
For a round rotor machine LB is small and hence Lmd is close to Lmq. For a salient pole machine Lmd is substantially
larger

## Slide 19: Convert to Normalized at f = ws
Convert to per unit, and assume frequency of ws
Then define new per unit reactance variables

## Slide 20: Example Xd/Xq Ratios for a WECC Case

## Slide 21
Normalized Equations

## Slide 22: Key Simulation Parameters
The key parameters that occur in most models can then be defined the following transient values
These values will be used in all the synchronous machine
models
In a salient rotor machine Xmq is small so Xq = X'q; also X1q is small so T'q0 is small

## Slide 23: Example X'q/Xq Ratios for a WECC Case
About 75% are Clearly Salient Pole Machines!

## Slide 24: Key Simulation Parameters
And the subtransient parameters
These values will be used in the subtransient machine models. It is common to assume X"d = X"q

## Slide 25
Internal Variables
Define the following variables, which are quite important in subsequent models
Hence E'q and E'd are scaled flux linkages and Efd is the scaled field voltage

## Slide 26: Dynamic Model Development
In developing the dynamic model not all of the currents and fluxes are independent
  In the book formulation only seven out of fourteen are independent
Approach is to eliminate the rotor currents, retaining the terminal currents (Id, Iq, I0) for matching the network boundary conditions

## Slide 27
Rotor Currents
Use new variables to solve for the rotor currents

## Slide 28
Rotor Currents

## Slide 29
Final Complete Model

## Slide 30
Final Complete Model
TFW is the friction and windage component that we'll consider later

## Slide 31
Final Complete Model

## Slide 32: Single-Machine Steady-State
Previous derivation was done assuming a linear magnetic circuit
We'll consider the nonlinear magnetic circuit (section 3.5) but will first do the steady-state condition (3.6)
In steady-state the speed is constant (equal to ws), d is constant, and all the derivatives are zero
Initial values are determined from the terminal conditions: voltage magnitude, voltage angle, real and reactive power injection

## Slide 33
Single-Machine Steady-State
The key variable we need to determine the initial conditions is actually d, which doesn't appear explicitly in these equations!

## Slide 34: Field Current
The field current, Ifd, is defined in steady-state as
However, what is usually used in transient stability simulations for the field current is
So the value of Xmd is not needed

## Slide 35
Determining d without Saturation
In order to get the initial values for the variables we need to determine d
We'll eventually consider two approaches: the simple one when there is no saturation, and then later a general approach for models with saturation
To derive the simple approach we have

## Slide 36: Determining d without Saturation
Recalling the relation between d and the stator values
We then combine the equations for Vd and Vq and get

## Slide 37: Determining d without Saturation
Then in terms of the terminal values