## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 9: Synchronous Machines,
Reduced-Order Models

## Slide 2: Announcements
Homework 2 is posted on the web; it is due on Thursday Feb 20
Read Chapter 5 and Appendix A
Read Chapter 6
A key paper for today's topic is P.V. Kokotovic, and P.W. Sauer, "Integral Manifold as a Tool for Reduced-Order Modeling of Nonlinear Systems: A Synchronous Machine Case Study," IEEE Trans. Circuits and Sys., March 1989
  "Make it as simple as possible but not simpler"

## Slide 3: Determining d without Saturation
Recalling the relation between d and the stator values
And from 3.215 and 3.216 (in steady-state)
Then use 3.222 and 3.223 to replace

## Slide 4: Determining d without Saturation
And use 3.219 to eliminate E'd

## Slide 5: Determining d without Saturation
Which can be rewritten as

## Slide 6: Determining d without Saturation
Then in terms of the terminal values

## Slide 7: D-q Reference Frame
Machine voltage and current are “transformed” into the d-q reference frame using the rotor angle, 
  Terminal voltage in network (power flow) reference frame are VS = Vt = Vr +jVi

## Slide 8: A Steady-State Example
Assume a generator is supplying 1.0 pu real power at 0.95 pf lagging into an infinite bus at 1.0 pu voltage through the below network. Generator pu values are Rs=0, Xd=2.1, Xq=2.0, X'd=0.3, X'q=0.5

## Slide 9: A Steady-State Example, cont.
First determine the current out of the generator from the initial conditions, then the terminal voltage

## Slide 10: A Steady-State Example, cont.
We can then get the initial angle and initial dq values
Or

## Slide 11: A Steady-State Example, cont.
The initial state variable are determined by solving with the differential equations equal to zero.

## Slide 12: PowerWorld Two-Axis Model
Numerous models exist for synchronous machines, some of which we'll cover in-depth. The following is a relatively simple model that represents the field winding and one damper winding; it also includes the generator swing eq.
For a salient pole machine, with Xq=X'q, then E'd would rapidly decay to zero

## Slide 13: PowerWorld Solution of 11.10

## Slide 14: Nonlinear Magnetic Circuits
Nonlinear magnetic models are needed because magnetic materials tend to saturate; that is, increasingly large amounts of current are needed to increase the flux density
Linear

## Slide 15
Saturation

## Slide 16: Saturation Models
Many different models exist to represent saturation
  There is a tradeoff between accuracy and complexity
Book presents the details of fully considering saturation in Section 3.5
One simple approach is to replace
With

## Slide 17: Saturation Models
In steady-state this becomes
Hence saturation increases the required Efd to get a desired flux
Saturation is usually modeled using a quadratic function, with the value of Se specified at two points (often at 1.0 flux and 1.2 flux)
A and B are determined from the two data points

## Slide 18: Saturation Example
If Se = 0.1 when the flux is 1.0 and 0.5 when the flux is 1.2, what are the values of A and B using the

## Slide 19: Implementing Saturation Models
When implementing saturation models in code, it is important to recognize that the function is meant to be positive, so negative values are not allowed
In large cases one is almost guaranteed to have special cases, sometimes caused by user typos
  What to do if Se(1.2) < Se(1.0)?
  What to do if Se(1.0) = 0 and Se(1.2) <> 0
  What to do if Se(1.0) = Se(1.2) <> 0
Exponential saturation models have been used
We'll cover other common saturation approaches in Chapter 5

## Slide 20: Reduced Order Models
Before going further, we will consider a formal approach to reduce the model complexity
  Reduced order models
Idea is to approximate the behavior of fast dynamics without having to explicitly solve the differential equations
  Essentially all models have fast dynamics that not explicitly modeled
Goal is a more easily solved model (i.e., a reduced order model) without significant loss in accuracy

## Slide 21: Manifolds
Hard to precisely define, but "you know one when you see one"
  Smooth surfaces
  In one dimensions a manifold is a curve without any kinks or self-intersections (line, circle, parabola, but not a figure 8)

## Slide 22
Two-Dimensional Manifolds
Images from book and mathworld.wolfram.com

## Slide 23
Suppose we could find z = h(x)
Integral Manifolds
Desire is to express z as an
algebraic function of x, eliminating dz/dt

## Slide 24
Integral Manifolds
Replace z by h(x)
If the initial conditions satisfy h, so z0 = h(x0) then the reduced equation is exact
Chain rule of differentiation

## Slide 25: Integral Manifold Example
Assume two differential equations with z considered "fast" relative to x

## Slide 26: Integral Manifold Example
For this simple system we can get the exact solution

## Slide 27
Solve for Equilibrium (Steady-state ) Values

## Slide 28: Solve for Remaining Constants
Use the initial conditions and derivatives at t=0 to solve for the remaining constants

## Slide 29
Solve for Remaining Constants

## Slide 30: Solution Trajectory in x-z Space
Below image shows some of the solution trajectories of this set of equations in the x z space
z rapidly decays to 1.0

## Slide 31: Candidate Manifold Function
Consider a function of the form z = h(x) = mx + c
We would then have
One equation and two unknowns: One solution is m=0, c=1

## Slide 32: Candidate Manifold Function
With the manifold z = 1 we have an exact solution if z = 1.0 since dz/dt = -10z+10 is always zero
With this approximation then we simplify as
This is exact only if z0 = 1.0
Exact solution

## Slide 33: Linear Function, Full Coupling
Now consider the linear function

## Slide 34: Linear Function, Full Coupling
Which has an equilibrium point at the origin, eigenvalues l1 = -2.3 (the slow mode) and l2 = -8.7 (the fast mode), and a solution of the form
Using x0 = 10 and z0 = 10, the solution is

## Slide 35: Solution Trajectory in x-z Space

## Slide 36: Linear Function, Full Coupling
Same function but change the initial condition to x0 = 0 and z0 = 10
Solving for the constants gives
In general

## Slide 37: Solution Trajectories in x-z Space

## Slide 38: Candidate Manifold Function
Trajectories appear to be heading to origin along a single axis
Again consider a candidate manifold function z = h(x) = mx + c
Again solve for m dx/dt

## Slide 39: Candidate Manifold Function

## Slide 40: Candidate Manifold Function
The two solutions correspond to the two modes
The one we've observed is z = -1.3x
The other is z = -7.7x
To observe this mode select x0 = 1 and z0 = -7.7
Zeroing out c1 and c3 is clearly a special case

## Slide 41: Eliminating the Fast Mode
Going with z = -1.3x we just have the equation
This is a simpler model, with the application determining whether it is too simple

## Slide 42: Formal Two Time-Scale Analysis
This can be more formalized by introducing a parameter e
In the previous example we had e = 0.1

## Slide 43: Formal Two Time-Scale Analysis
Using the previous process to get an expression for dx/dt we have
For c(e) = 0
Result is complex for larger values since system has complex eigenvaues

## Slide 44: Formal Two Time-Scale Analysis
If z is infinitely fast (e = 0) then z = -x, h(e) = -1
To compute for small e use a power series

## Slide 45: Formal Two Time-Scale Analysis
Solving for the coefficients

## Slide 46
Applying to the Previous Example
Note the slow mode eigenvalue approximation has changed from -2.3 to -2.2

## Slide 47: General two-time-scale linear system
To generalize assume
Expression for z is the equilibrium manifold; D must be nonsingular

## Slide 48: Application to Nonlinear Systems
For machine models this needs to be extended to nonlinear systems
In general solution is difficult, but there are special cases similar to the stator transient problem

## Slide 49
Example

## Slide 50: Example
Solving we get